## Tank_Template
ABOVEGROUND STORAGE TANK THICKNESS SURVEY
TANK IDENTIFICATION
Tank No: |  |  | Height: |  |  | Shell Material:
Service: |  |  | Year Built: |  |  | Floor Material:
Capacity: |  |  | Roof Type: |  |  | Last Inspection:
Diameter: |  |  | Floor Type: |  |  | Inspection Type:
SHELL THICKNESS READINGS (mm)
Course | Original Thk (mm) | N | NE | E | SE | S | SW | W | NW | Minimum | t-min (mm)
1
2
3
4
5
6
7
8
FLOOR THICKNESS READINGS (mm) - See attached sketch for grid reference
Grid | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | Min
A
B
C
D
E
F
G
H
ANNULAR PLATE READINGS (mm)

## Tank_Sample_T501
ABOVEGROUND STORAGE TANK THICKNESS SURVEY
TANK IDENTIFICATION
Tank No: | T-501 |  | Height: | 48 ft (14.6m) |  | Shell Material: | A36
Service: | Crude Oil Storage |  | Year Built: | 1985 |  | Floor Material: | A36
Capacity: | 50,000 BBL |  | Roof Type: | External Floating |  | Last Internal: | 2021-08-15
Diameter: | 120 ft (36.6m) |  | Floor Type: | Cone Up (on ringwall) |  | Inspection Type: | Internal (Out of Service)
Inspector: K. Thompson Date: 2026-01-15 Instrument: Olympus 38DL+ S/N 34567
SHELL THICKNESS READINGS (mm)
Course | Original (mm) | N | NE | E | SE | S | SW | W | NW | Min | t-min (mm) | Status
1 | 25.4 | 22.15 | 22.08 | 21.95 | 22.12 | 22.18 | 21.88 | 22.05 | 22.11 | 21.88 | 12.7 | Good
2 | 22.23 | 19.85 | 19.92 | 19.78 | 19.88 | 19.95 | 19.72 | 19.82 | 19.91 | 19.72 | 11.12 | Good
3 | 19.05 | 17.25 | 17.18 | 17.08 | 17.22 | 17.28 | 17.02 | 17.15 | 17.21 | 17.02 | 9.53 | Good
4 | 15.88 | 14.52 | 14.48 | 14.38 | 14.55 | 14.58 | 14.32 | 14.45 | 14.51 | 14.32 | 7.94 | Good
5 | 12.7 | 11.85 | 11.78 | 11.68 | 11.82 | 11.88 | 11.62 | 11.75 | 11.81 | 11.62 | 6.35 | Good
6 | 9.53 | 8.92 | 8.85 | 8.75 | 8.88 | 8.95 | 8.68 | 8.82 | 8.88 | 8.68 | 4.76 | Good
7 | 9.53 | 8.88 | 8.82 | 8.72 | 8.85 | 8.91 | 8.65 | 8.78 | 8.85 | 8.65 | 4.76 | Good
8 | 9.53 | 8.95 | 8.88 | 8.78 | 8.92 | 8.98 | 8.72 | 8.85 | 8.92 | 8.72 | 4.76 | Good
FLOOR THICKNESS READINGS (mm) - See attached sketch for grid
Grid | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | Row Min
A | 5.82 | 5.78 | 5.85 | 5.75 | 5.88 | 5.72 | 5.81 | 5.79 | 5.72
B | 5.75 | 5.68 | 5.72 | 5.65 | 5.78 | 5.62 | 5.71 | 5.69 | 5.62
C | 5.88 | 5.82 | 5.78 | 5.71 | 5.85 | 5.68 | 5.82 | 5.78 | 5.68
D | 5.72 | 5.65 | 5.58 | 4.85 | 5.68 | 5.52 | 5.65 | 5.62 | 4.85
E | 5.78 | 5.72 | 5.68 | 5.62 | 5.75 | 5.58 | 5.72 | 5.68 | 5.58
F | 5.85 | 5.78 | 5.75 | 5.68 | 5.82 | 5.65 | 5.78 | 5.75 | 5.65
G | 5.92 | 5.85 | 5.82 | 5.75 | 5.88 | 5.72 | 5.85 | 5.82 | 5.72
H | 5.88 | 5.82 | 5.78 | 5.72 | 5.85 | 5.68 | 5.81 | 5.78 | 5.68
ANNULAR PLATE READINGS (mm) - Original: 12.70mm, t-min: 6.35mm
Location | N | NE | E | SE | S | SW | W | NW
Inner Edge | 11.52 | 11.48 | 11.42 | 11.55 | 11.58 | 11.38 | 11.45 | 11.51
Mid | 11.68 | 11.62 | 11.55 | 11.71 | 11.75 | 11.52 | 11.61 | 11.68
Outer Edge | 11.85 | 11.78 | 11.72 | 11.88 | 11.92 | 11.68 | 11.78 | 11.85
NOTES:
- Floor reading D4 (4.85mm) indicates localized pitting. Mark for monitoring or repair.
- Original floor thickness: 6.35mm, t-min per API 653: 2.54mm (0.1")
- All shell courses within acceptable limits. Next shell inspection: 10 years.